Attachment 1

Cooling Tower System

Risk Management Plan Template

Components and Format of a risk management plan

Generally a risk management plan should have a number of basic components that would include:

- Site and contact details

- Assessment of each of the critical risks

- Summary of the overall risk classification

- Details of the system collected during the risk assessment process

- Attachments or reference to other documents such as operational plans, shut-down procedures and so on.

Whilst there is no prescribed format for a risk management plan this template is provided as a guide. Other formats may, of course, be used.

About the Template

The template is designed to be completed:

- By cooling tower system operators or land owners who have cooling tower systems on their land.

- After first reading the preceding Guide.

- After completing a thorough risk assessment as outlined in the Guide.

This process will meet the requirements of the Public Health and Wellbeing Act 2008 in terms of the development of a risk management plan.

A risk management plan must be developed for every cooling tower system on the site. The Plan once developed must be made available to an authorised officer of the Department of Health on request.

Implementation of an Operational Program outlined in the risk management plan would also meet the requirements of the Public Health and Wellbeing Regulations 2009.

The template is also available in Word format at  www.health.vic.gov.au/environment/legionella and can be modified to use in the development of your plan.

Disclaimer

This document is intended only as a general guide to the development of Risk Management Plans for Cooling Tower Systems. No warranty as to the completeness of the information is given. The Department of Health and its employees disclaim all liability and responsibility for any direct or indirect loss or damage which may be suffered through reliance on any information contained in or omitted from this document, and no person should act solely on the basis of the information contained in the document without taking appropriate professional advice about obligations in specific circumstances.

# Site and Key Contact Details

| Record | Your details |
| --- | --- |
| Site location (property address) |  |
| Number of cooling towers in system |  |
| Cooling Tower System Number |  |
| Tower location reference (If one exists) |  |
| Site owner’s name/contact details (Include company name, contact person’s business and after hours telephone numbers) |  |
| Cooling tower system owner’s name/contact details (Include company name, contact person’s business and after hours telephone numbers) |  |
| Who is responsible for day-to-day operation of the cooling tower system? (Include company name, contact person’s business and after hours telephone numbers) |  |
| Water treatment provider name/contact details (Include company name, contact person’s business and after hours telephone numbers) |  |
| Water sampling/laboratory contractor/contact details (Include company name, contact person’s business and after hours telephone numbers) |  |
| Department of Health Legionella Team | 1800 248 898 |

# Critical Risks

## 1.1 	Stagnant Water

| Stagnant Water Risk Control Strategy | Assessment of the cooling tower system (Tick box) | Operational or Tower System Improvement Response |
| --- | --- | --- |
| Installation of a timer connected to a recirculating pump set to operate at least once a day to circulate the water | Is the system (or part of the system) idle for more than a month? □ Yes □ No |  |
|  | Where the system (or part of the system) is idle for more than a month, is a recirculating pump with a timer fitted to automatically circulate the water at regular intervals, to prevent it becoming stagnant? □ Yes □ No |  |
| Removal or activation of any ‘dead legs’ | Are there ‘dead legs’ in the system? □ Yes □ No |  |
| Other |  |  |

| Risk Classification for Stagnant Water Risk | □ A □ B □ C □ D |
| --- | --- |

## 1.2		Nutrient Growth

| Nutrient Growth Risk Control Strategy | Assessment of the Cooling Tower System | Operational or Tower system Improvement Response |
| --- | --- | --- |
| Identify sources of, and where possible, reduce the amount of environmental contamination | Are there factors in and around the site that may lead to environmental contamination and an increase in the level of nutrients in the cooling tower system? □Yes □No |  |
|  | If Yes, can you reduce the levels of contamination? □Yes □No |  |
| Use a comprehensive water treatment program that includes a bio-dispersant | Do you use a bio-dispersant compatible with the chemicals in use (including chlorine) □Yes □No |  |
| Control corrosion | Do you have a corrosion control program? □Yes □No |  |
| Increase the frequency of cleaning | How frequently is the tower cleaned? ……………………………………… |  |
| Protect the basin and ‘top deck’ of the tower from sunlight | Are any of the wetted surfaces exposed to sunlight? □Yes □No |  |
| Reduce the water temperature where possible | Can the water temperature of the tower be reduced? □Yes □No |  |
| Other |  |  |

| Risk Classification for Nutrient Growth Risk | □ A □ B □ C □ D |
| --- | --- |

## 1.3  	Poor Water Quality

| Poor Water Quality Risk Control Strategy | Assessment of the Cooling Tower System | Operational or Tower System Improvement Response |
| --- | --- | --- |
| Comprehensive water treatment program | Do you use two or more biocides in some form of rotation? □Yes □No |  |
|  | Do you use a bio-dispersant compatible with the chemicals in use (including chlorine)? □Yes □No |  |
|  | Do you treat the water with anti-corrosive chemicals? □Yes □No |  |
|  | Have you developed control measures that are frequently measured to confirm that the water chemistry is under control? □Yes □No |  |
| Testing for HCC | How frequently do you test for HCC? |  |
| Testing for Legionella | How frequently do you test for Legionella? |  |
| Managing HCC levels | What HCC level do you allow before you take remedial action? □ 200,000 cfu/mL □ A number less than 200,000 cfu/mL |  |
| Response to high HCC results | How do you respond to a high HCC test result? □ We follow Attachment A □ We follow Attachment B □ We follow our own response plan |  |
| Response to the detection of Legionella | How do you respond to Legionella being detected in a sample? □ We follow Attachment C □ We follow an alternative plan which still meets the requirements of the Regulations |  |
| Labelling of the cooling tower system | Is the cooling tower and cooling tower system labelled with the CTS registration number? □ Yes □ No |  |
| Appropriate bleed-off rates to prevent a build-up of solids | Is an automated bleed-off device installed? □Yes □No |  |
| Install automated biocide dosing device | Do you have an automated biocide dosing device? □Yes □No |  |
| Install automated dosing devices for all chemicals or agents | Do you have automated dosing devices for all chemicals/agents? □Yes □No |  |
| Selection of an appropriate point for chemical dosing | Does the chemical dosing occur well away from where the sampling point for bacterial tests is taken? □Yes □No |  |
| Provision of a dedicated water sampling point | Are water samples always taken from the same point? □Yes □No |  |
|  | If Yes, is that point clearly labelled with the cooling tower system registration identification number (CTS ID)? □Yes □No |  |
|  | Has a sampling tap been fitted? □Yes □No |  |
| Install a side stream filter if environment is dirty | Is the environment around the tower dirty? □Yes □No |  |
|  | If yes, do you have a side stream filter? □Yes □No |  |
| Other |  |  |

| Risk Classification for Poor Water Quality Risk | □ A □ B □ C □ D |
| --- | --- |

## 1.4	Deficiencies in the Cooling Tower System

| Deficiencies in the Cooling Tower System Risk Control Strategy | Assessment of the Cooling Tower System | Operational or Tower System Improvement Response |
| --- | --- | --- |
| Review the system design against AS/NZS 3666 | Has a review been conducted? □Yes □No |  |
|  | Are there any improvements that can be made to the system design to reduce risks? □Yes □No |  |
| Review current performance of system | Has a review been conducted? □Yes □No |  |
| Develop operating and maintenance manuals | Are operating and maintenance manuals developed? □Yes □No |  |
| Review the useful life of the system and plan to replace it at an appropriate time | When was the tower built? |  |
|  | Do you have a program to replace it? □Yes □No |  |
| Install a modern high efficiency drift eliminator | Is there a modern high efficiency drift eliminator fitted to every tower in the system? □Yes □No |  |
|  | Are the drift eliminators in good condition? □Yes □No |  |
|  | Have the drift eliminators been certified by the manufacturer as meeting AS/NZS 3666? □Yes □No |  |
| Use suitable materials for external components | Have you reviewed the condition of the tower structure? □Yes □No |  |
| Use suitable materials for internal components | Have you reviewed the materials and condition of the internal components of the tower system? □Yes □No |  |
| Other |  |  |

| Risk Classification for Deficiencies in the Cooling Tower System Risk | □ A □ B □ C □ D |
| --- | --- |

## 1.5		Location and Access

| Location and Access Risk Control Strategy | Assessment of the Cooling Tower System | Operational or Tower System Improvement Response |
| --- | --- | --- |
| Understand the extent of potential exposure to the cooling tower | Is the cooling tower system located in an acute health or aged residential care facility? □Yes □No |  |
|  | If No, is the cooling tower system located within 500m of an acute health or aged residential care facility? □Yes □No |  |
| Minimise access to tower and surrounds | How many people have access to the tower and its surrounds? □ Very high numbers □ High numbers… □ Moderate numbers □ Low numbers |  |
|  | Are warning signs displayed around the tower? □Yes □No |  |
|  | Is the area around the cooling tower system used as a gathering place for staff and visitors, particularly smokers? □Yes □No |  |
|  | Is access to the tower restricted? □Yes □No |  |
| Relocation of tower to more remote site or less contaminated environment (where possible) | Have you reviewed whether it is possible to relocate the tower to a safer location? □Yes □No |  |
| Ensure there is a safe and stable area for maintenance workers to access the cooling tower system | Have you reviewed the working environment for maintenance workers? □Yes □No |  |
| Other |  |  |
| Risk Classification for Location and Access Risk | □ A □ B □ C □ D |

# Risk Assessment Summary

| Critical Risk Classification |
| --- |
| Stagnant Water | □ A □ B □ C □ D |
| Nutrient Growth | □ A □ B □ C □ D |
| Poor Water Quality | □ A □ B □ C □ D |
| Deficiencies in the Cooling Tower System | □ A □ B □ C □ D |
| Location and Access | □ A □ B □ C □ D |
| Are there any other considerations that may affect the overall risk assessment of the cooling tower system? |  |
| Overall Cooling Tower System Risk Classification Category | □ A |
|  | □ B |
|  | □ C |
|  | □ D |

# 3 Attachments

# 4 Operational Program

| Recommended Operational Programs based on Risk Classification |
| --- |
| Program A | Program B | Program C | Program D |
| Weekly inspection | Monthly inspection (two weeks after service) | Monthly inspection (two weeks after service) | Monthly service |
| Fortnightly service | Monthly service | Monthly service |  |
| HCC and Legionella tested at a minimum of once each month. | HCC and Legionella tested monthly | HCC tested monthly. Legionella tested every two months | HCC tested monthly. Legionella tested every three months |
| Six monthly cleaning, or more frequently where environmental contamination (for example dust, soil, building works etc) is a problem |

| Element | Tick box |
| --- | --- |
| Describe your maintenance program? | □ Department of Health Program A |
|  | □ Department of Health Program B |
|  | □ Department of Health Program C |
|  | □ Department of Health Program D |
|  | □ Self-developed |
|  | □ Developed by consultant |
| If self-developed or developed by consultant, complete remainder of table |
| Service frequency | □ Weekly |
|  | □ Fortnightly |
|  | □ Monthly |
| HCC testing frequency | □ Monthly |
|  | □ Every …….. week/s |
| Legionella testing frequency | □ Every three months □ Every …….. weeks/months |
| Tower cleaning frequency (select one and fill in blank if appropriate) | □ Every 6 months |
|  | □ Every …….. months |
| Inspection frequency | □ Every ………… weeks/month |

# 5 Monitoring and Review

| Element | Details |
| --- | --- |
| Date RMP due for review |  |
| Name/Title of person responsible for review |  |
| Date RMP reviewed |  |
| Does the RMP require amendment? | □Yes |
|  | □No |
| Was the review conducted as a result of a triggering event occurring? |  |  |
| If RMP requires amendment, date amendments due and completed? | Due |  |
|  | Completed |  |

# 6 Communication

| Element | Details |
| --- | --- |
| List parties (names and contact details) who will be informed in the event of a positive Legionella test | Category | Name/Title | Telephone | Comment |
|  | Staff |  |  |  |
|  | Occupational health staff/contractors |  |  |  |
|  | Unions |  |  |  |
|  | Building owner |  |  |  |
|  | Other building occupiers |  |  |  |
|  | Medical officer |  |  |  |
|  | Staff counsellors |  |  |  |
|  | Department of Health, Legionella Team |  | 1800 248 898 |  |
|  | Media Liaison Officer |  |  |  |
|  | Company spokesperson |  |  |  |
|  | Chief Executive |  |  |  |

# 7 Endorsement of Risk Management Plan

| Name/position of person responsible for Risk Management Plan |  |
| --- | --- |
| Signature |  |
| Date |  |

# Footnotes

This is marked on the Certificate of Registration supplied by the Department of Health.

This person has the authority to approve the disinfection of the system on request of the Department of Health. It is not the water treatment service provider.

Indicate the operational program or improvements you will put in place as a result of this assessment.

If you do not have a recirculating pump and timer installed you can address the risk by installing such a pump. You should state the date that the pump will be installed. If you do not propose to install such a pump, then you should describe how you will address the risk in the response column.

Use this row to describe other risks and response strategies that relate to this risk.

Refer to Figure 12 in Section 6.2.2 of the guide and find the scenario that matches your system to evaluate the risk associated with stagnant water and your system.

Describe the strategies in the response column.

Describe how you will address the risk in the response column.

The Public Health and Wellbeing Regulations 2009 requires that the system is continuously treated with a bio-dispersant.

The Public Health and Wellbeing Regulations 2009 require the use of a chlorine compatible bio-dispersant as part of the disinfection, cleaning and re-disinfection process, (as a minimum) prior to initial start up or any shut down period of greater than one month and at intervals not exceeding six months.

The Public Health and Wellbeing Regulations 2009 require the treatment of the cooling tower system water with chemicals or other agents to minimise corrosion.

The Public Health and Wellbeing Regulations 2009 require the disinfection, cleaning and re-disinfection process to be performed prior to initial start up or any shut down period of greater than one month and at intervals not exceeding six months.

Describe how you will address the risk in the response column.

You should describe how and when you will reduce the temperature in the response column.

Describe how you will address the risk in the response column.

Use this row to describe other risks and response strategies that relate to this risk.

Refer to Table in Section 6.2 of the Guide and find the scenario that matches your system to evaluate the risk associated with Nutrient Growth and your system.

Indicate the operational program you will put in place as a result of this assessment.

The use of two biocides is recommended as a way to minimise the risks of bacteria becoming resistant to the biocide.

The Public Health and Wellbeing Regulations 2009 requires that the system is continuously treated with a bio-dispersant.

The Public Health and Wellbeing Regulations 2009 require the use of a chlorine compatible bio-dispersant as part of the disinfection, cleaning and re-disinfection process, (as a minimum) prior to initial start up or any shut down period of greater than one month and at intervals not exceeding six months.

The Public Health and Wellbeing Regulations 2009 require the treatment of the cooling tower system water with chemicals or other agents to minimise corrosion

Describe these in the response column.

The monitoring of control measures can increase your confidence that the system is under control and can provide early warning when it is not. Describe how you will address the risk in the response column.

The Department recommends every cooling tower system be tested regularly for Legionella as per Section 7.4 of the RMP Guide. The Public Health and Wellbeing Regulations 2009 require a minimum of quarterly testing for Legionella.

If you do use a lower number than 200,000cfu/mL then you must detail the number in the Operational Response column

This refers to the ‘Attachment A – Standard HCC Sampling and Response’ which summarise aspects of the requirements of the Public Health & Wellbeing Regulations 2009.

This refers to the ‘Attachment B – Alternative HCC Sampling and Response’ which summarise aspects of the requirements of the Public Health & Wellbeing Regulations 2009.

Any alternative plan must incorporate the minimum requirements of the Public Health & Wellbeing Regulations 2009. The operational response column must describe the plan n detail.

The Public Health and Wellbeing Regulations 2009 require that action is taken following the detection of Legionella

This refers to the ‘Attachment C – Legionella Sampling and Response’ which summarise aspects of the requirements of the Public Health & Wellbeing Regulations 2009.

The Operational Response must detail the process that you will follow.

The Operational Response must describe where the label appears on the system. It is recommended that you use a system where a tower is labelled with the CTS ID e.g. ‘1234’ followed by a ‘slash’ and then a number or other identifying mark to describe the tower e.g. ‘1234/1’ would designate Tower 1 of system 1234

The Operational Response must describe how you will deal with the risk that there may be confusion as to which tower or which system is being referred to in service reports or laboratory test results amongst other things

Best practice is the use of conductivity controlled meters fitted with lock out devices to prevent excessive loss of chemicals during the bleed-off process.

Describe how you will address the risk of poor water quality in the response column.

Best practise is the use of electronic programmable automated dosing units.  You should describe how you will address the risks of biocide failure in the response column.

Best practise is the use of electronic programmable automated dosing units. You should describe how you will address the risks of inadequate chemical dosing in the response column.

You should modify your sampling program to ensure you are getting representative results.

This number is printed on your Certificate of Registration.

Describe how you will address the risk in the response column.

Use this row to describe other risks and response strategies that relate to this risk.

Refer to Figure 12 in Section 6.2.2 and find the scenario that matches your system to evaluate the risk associated with poor water quality and your system.

Indicate the operational program you will put in place as a result of this assessment.

Describe how you will address the risk in the response column.

Describe the improvements in the response column.

Describe how you will address the risk in the response column.

Describe the improvements in the response column.

Without a review, it is impossible to complete a proper risk assessment.  Describe how you will address the risks without the review in the response column.

Describe how you will address the risks in the response column.

Describe when in the response column.

Describe how you will address the risks in the response column.

Describe how you will address the risks of excessive drift leaving the towers in the response column. for example by installing a drift eliminator that complies with AS/NZS 3666.

Describe how you will address the risks of excessive drift leaving the towers in the response column, for example by installing a drift eliminator that complies with AS/NZS 3666.

Describe how you will address the risks of excessive drift leaving the towers in the response column, for example by installing a drift eliminator that complies with AS/NZS 3666.

Describe the improvements in the response column.

Describe how you will address the risk in the response column.

Describe the improvements in the response column.

Describe how you will address the risk in the response column.

Use this row to describe other risks and response strategies that relate to this risk.

Refer to Figure 12 in Section 6.2.2 of the guide and find the scenario that matches your system to evaluate the risk associated with deficiencies in the cooling tower system and your system.

Indicate the operational program you will put in place as a result of this assessment.

Classify as Risk Category A and respond with highest standards of maintenance and surveillance.

Classify as a minimum of Risk Category B and respond with high standards of maintenance and surveillance.

You should consider the surroundings within 500m of the cooling tower

Refer to Figure 10 of Guide to Developing Risk Management Plans for Cooling Tower Systems.

Refer to Figure 10 of Guide to Developing Risk Management Plans for Cooling Tower Systems.

Refer to Figure 10 of Guide to Developing Risk Management Plans for Cooling Tower Systems.

Refer to Figure 10 of Guide to Developing Risk Management Plans for Cooling Tower Systems.

For example, ‘Authorised Persons Only’.

Describe how you will address the risks without such signs.

Describe how you will address the risks of smokers being in close proximity to the cooling towers.

Describe how you will address the risks until access to the tower has been restricted.

Describe outcomes of the review.

Describe how you will address the risk of location and access without such a review.

This is a key area in terms of meeting your responsibilities under the Occupational Health and Safety Act.

Describe the outcomes of the review. For example, any actions to be taken.

Describe how you will address the risks without such a review.

Use this row to describe other risks and response strategies that relate to this risk.

Refer to Figure 12 in Section 6.2.2 of the guide and find the scenario that matches your system to evaluate the risk associated with location and access and your system.

Tick the appropriate box based on your responses to the questions in Figure 12 in Section 6.2.2 of the Guide.

Other information which can be appended to the Risk Management Plan includes site plan, photographs, schematics of water flows, cooling tower makes and models, basic system parameters, for example system volume, system heat rejection capacity and system operating temperature.

Select one and fill in blank if appropriate

Under section 92(2) of the Public Health and Wellbeing Act 2008, the owner of the land must also take all reasonable steps to ensure that the risk management plan is reviewed, and if necessary updated, if-

- legionella is detected in the cooling tower system on 2 or more occasions in any period of 12 months; or

- the owner of the land is given written advice by the Secretary that a case of legionnaires’ disease is associated with thee cooling tower system; or

- the owner of the land receives a report from the Secretary or from any person engaged by the owner of the land or the owner of the cooling tower system that control measures used in respect of the cooling tower system are inadequate or require improvement; or

- there is a significant change in-

  - any of the environmental conditions under which the cooling tower system operates; or

  - the operation of the cooling tower system; or

- the owner of the land receives an audit certificate that states that the risk management plan does not address the prescribed risks.

# Endnotes

Indicate the operational program you will put in place as a result of this assessment